## Plt1
FriendlyName | Units | DataPointName | PointType
AddShedSource | NULL | AddShedSource | Unknown Type
CDWVLV | 0-100% | CDWVLV | BAS
CDWVLV2 | Amps | CDWVLV2 | BAS
Total Chiller kW | kW | CHkW | BAS
CHW Differential Pressure #2 | PSI | CHWDP2 | BAS
Chilled Water Flow | GPM | CHWFLO | BAS
Chilled Water Return Temperature | °F | CHWRT | BAS
Chilled Water Return Temperature 2 | °F | CHWRT2 | BAS
Chilled Water Return Temperature 3 | °F | CHWRT3 | BAS
Chilled Water Supply Temperature | °F | CHWST | BAS
Chilled Water Supply Temperature 2 | °F | CHWST2 | BAS
Chilled Water Supply Temperature 3 | °F | CHWST3 | BAS
Chilled Water Valve Position #10 | 0-100% | CHWV10 | BAS
Chilled Water Valve Position #11 | 0-100% | CHWV11 | BAS
Chilled Water Valve Position #12 | 0-100% | CHWV12 | BAS
Chilled Water Valve Position #13 | 0-100% | CHWV13 | BAS
Chilled Water Valve Position #14 | 0-100% | CHWV14 | BAS
Chilled Water Valve Position #15 | 0-100% | CHWV15 | BAS
Chilled Water Valve Position #16 | 0-100% | CHWV16 | BAS
Chilled Water Valve Position #17 | 0-100% | CHWV17 | BAS
Chilled Water Valve Position #18 | 0-100% | CHWV18 | BAS
Chilled Water Valve Position #19 | 0-100% | CHWV19 | BAS
Chilled Water Valve Position #20 | 0-100% | CHWV20 | BAS
Chilled Water Valve Position #21 | 0-100% | CHWV21 | BAS
Chilled Water Valve Position #22 | 0-100% | CHWV22 | BAS
Chilled Water Valve Position #23 | 0-100% | CHWV23 | BAS
Chilled Water Valve Position #24 | 0-100% | CHWV24 | BAS
Chilled Water Valve Position #25 | 0-100% | CHWV25 | BAS
Chilled Water Valve Position #26 | 0-100% | CHWV26 | BAS
Chilled Water Valve Position #27 | 0-100% | CHWV27 | BAS
Chilled Water Valve Position #3 | 0-100% | CHWV3 | BAS
Chilled Water Valve Position #4 | 0-100% | CHWV4 | BAS
Chilled Water Valve Position #5 | 0-100% | CHWV5 | BAS
Chilled Water Valve Position #6 | 0-100% | CHWV6 | BAS
Chilled Water Valve Position #7 | 0-100% | CHWV7 | BAS
Chilled Water Valve Position #9 | 0-100% | CHWV9 | BAS
CLGMODE | Value | CLGMODE | BAS
CommunicationFailure | Normal/Alarm | CommunicationFailure | BAS
CommunicationFailure_COV | NULL | CommunicationFailure_COV | BAS
CTTR ALARM | Normal/Alarm | CTTR_ALARM | BAS
Heat Exchanger Condenser Water Return Temperature | °F | HX1CDWRT | BAS
Heat Exchanger Condenser Water Supply Temperature | °F | HX1CDWST | BAS
Heat Exchanger Condenser Water Valve (Binary) | 0-100% | HX1CDWVLV | BAS
Heat Exchanger Chilled Water Return Temperature | °F | HX1CHWRT | BAS
Heat Exchanger Chilled Water Supply Temperature | °F | HX1CHWST | BAS
Heat Exchanger Chilled Water Valve (Binary) | 0-100% | HX1CHWVLV | BAS
LOOPREQ | True/False | LOOPREQ | BAS
MaxCHDPLift | PSI | MaxCHDPLift | BAS
MaxCHDTLift | °F | MaxCHDTLift | BAS
MinCHDPLift | PSI | MinCHDPLift | BAS
MinCHDTLift | °F | MinCHDTLift | BAS
Outside Air Humidity | 0-100% | OAH | BAS
Outside Air Temperature | °F | OAT | BAS
Outside Air Wet Bulb Temperature | °F | OAWB | BAS
PCHWP Failed (BAS Alarm) | Normal/Alarm | PCHWP3Failed | BAS
PCHWP3HZ | Hz | PCHWP3HZ | BAS
PCHWP kW | kW | PCHWP3kW | BAS
PCHWP Status | Running/Off | PCHWP3S | BAS
PCHWP Speed Setting | 0-100% | PCHWP3SPD | BAS
PCHWP Start/Stop | Enable/Disable | PCHWP3SS | BAS
PCHWP Failed (BAS Alarm) | Normal/Alarm | PCHWP4Failed | BAS
PCHWP4HZ | Hz | PCHWP4HZ | BAS
PCHWP kW | kW | PCHWP4kW | BAS
PCHWP Status | Running/Off | PCHWP4S | BAS
PCHWP Speed Setting | 0-100% | PCHWP4SPD | BAS
PCHWP Start/Stop | Enable/Disable | PCHWP4SS | BAS
PCHWP Failed (BAS Alarm) | Normal/Alarm | PCHWP5Failed | BAS
PCHWP5HZ | Hz | PCHWP5HZ | BAS
PCHWP kW | kW | PCHWP5kW | BAS
PCHWP Status | Running/Off | PCHWP5S | BAS
PCHWP Speed Setting | 0-100% | PCHWP5SPD | BAS
PCHWP Start/Stop | Enable/Disable | PCHWP5SS | BAS
SCHWP Failed (BAS Alarm) | Normal/Alarm | SCHWP3Failed | BAS
SCHWP3HZ | Hz | SCHWP3HZ | BAS
SCHWP kW | kW | SCHWP3kW | BAS
SCHWP Status | Running/Off | SCHWP3S | BAS
SCHWP Speed Setting | 0-100% | SCHWP3SPD | BAS
SCHWP Start/Stop | Enable/Disable | SCHWP3SS | BAS
SCHWP Failed (BAS Alarm) | Normal/Alarm | SCHWP4Failed | BAS
SCHWP4HZ | Hz | SCHWP4HZ | BAS
SCHWP kW | kW | SCHWP4kW | BAS
SCHWP Status | Running/Off | SCHWP4S | BAS
SCHWP Speed Setting | 0-100% | SCHWP4SPD | BAS
SCHWP Start/Stop | Enable/Disable | SCHWP4SS | BAS
SCHWP Failed (BAS Alarm) | Normal/Alarm | SCHWP5Failed | BAS
SCHWP5HZ | Hz | SCHWP5HZ | BAS
SCHWP kW | kW | SCHWP5kW | BAS
SCHWP Status | Running/Off | SCHWP5S | BAS
SCHWP Speed Setting | 0-100% | SCHWP5SPD | BAS
SCHWP Start/Stop | Enable/Disable | SCHWP5SS | BAS
kW per Ton | kW/Ton | kW/Ton | Calculated
Chiller 3 CHWSTSP Alarm | Normal/Alarm | CH3_CHWSTSP_Alarm | Chiller
Chiller Failed (BAS Alarm) | Normal/Alarm | CH3ALARM | Chiller
CH3AVAIL | True/False | CH3AVAIL | Chiller
CH3Calc_ProjkW$2fTon | kW/Ton | CH3Calc_ProjkW$2fTon | Chiller
Condenser Refrigerant Pressure | PSI | CH3CDP | Chiller
Condenser Refrigerant Temperature | °F | CH3CDT | Chiller
CH3CDW_DeltaT | °F | CH3CDW_DeltaT | Chiller
Condenser Return Water Temperature | °F | CH3CDWRT | Chiller
Condenser Supply Water Temperature | °F | CH3CDWST | Chiller
CH3CHW_DeltaT | °F | CH3CHW_DeltaT | Chiller
Chiller Evaporator Flow | GPM | CH3CHWFLO | Chiller
Chilled Water Return Temperature | °F | CH3CHWRT | Chiller
Chilled Water Supply Temperature | °F | CH3CHWST | Chiller
Chilled Water Supply Temperature Setpoint | °F | CH3CHWSTSP | Chiller
Chiller CHW Valve Command (Binary) | Open/Close | CH3CHWVLV | Chiller
Compressor 1 General Fault | Normal/Alarm | CH3COM1F | Chiller
Compressor 1 IGV position / Vane Position | 0-100% | CH3COM1IGV | Chiller
Compressor 1 Status | Running/Off | CH3COM1S | Chiller
Compressor 1 Motor Speed / VFD Speed | 0-100% | CH3COM1SPD | Chiller
CH3CompDiscSuperheat | °F | CH3CompDiscSuperheat | Chiller
CH3CondApproach | °F | CH3CondApproach | Chiller
CH3DISTEMP | °F | CH3DISTEMP | Chiller
CH3DPLift | PSI | CH3DPLift | Chiller
CH3DTLift | °F | CH3DTLift | Chiller
CH3EvapApproach | °F | CH3EvapApproach | Chiller
Evaporator Refrigerant Pressure | PSI | CH3EVP | Chiller
Evaporator Refrigerant Temperature | °F | CH3EVT | Chiller
Chiller Alarm/Fault Msg | Normal/Alarm | CH3F | Chiller
CH3FLA | 0-100% | CH3FLA | Chiller
Total Chiller kW | kW | CH3kW | Chiller
CH3kW$2fTon | kW/Ton | CH3kW$2fTon | Chiller
CH3PctLoad | % | CH3PctLoad | Chiller
CH3Ready | True/False | CH3Ready | Chiller
Chiller Status | Running/Off | CH3S | Chiller
Chiller 3 SBoolean | On/Off | CH3SBoolean | Chiller
Chiller Start/Stop | Enable/Disable | CH3SS | Chiller
CH3SURGE | True/False | CH3SURGE | Chiller
CH3SURGECNT | Value | CH3SURGECNT | Chiller
CH3Tons | Ton | CH3Tons | Chiller
Chiller 4 CHWSTSP Alarm | Normal/Alarm | CH4_CHWSTSP_Alarm | Chiller
Chiller Failed (BAS Alarm) | Normal/Alarm | CH4ALARM | Chiller
CH4AVAIL | True/False | CH4AVAIL | Chiller
CH4Calc_ProjkW$2fTon | kW/Ton | CH4Calc_ProjkW$2fTon | Chiller
Condenser Refrigerant Pressure | PSI | CH4CDP | Chiller
Condenser Refrigerant Temperature | °F | CH4CDT | Chiller
CH4CDW_DeltaT | °F | CH4CDW_DeltaT | Chiller
Condenser Return Water Temperature | °F | CH4CDWRT | Chiller
Condenser Supply Water Temperature | °F | CH4CDWST | Chiller
CH4CHW_DeltaT | °F | CH4CHW_DeltaT | Chiller
Chiller Evaporator Flow | GPM | CH4CHWFLO | Chiller
Chilled Water Return Temperature | °F | CH4CHWRT | Chiller
Chilled Water Supply Temperature | °F | CH4CHWST | Chiller
Chilled Water Supply Temperature Setpoint | °F | CH4CHWSTSP | Chiller
Chiller CHW Valve Command (Binary) | Open/Close | CH4CHWVLV | Chiller
Compressor 1 General Fault | Normal/Alarm | CH4COM1F | Chiller
Compressor 1 IGV position / Vane Position | 0-100% | CH4COM1IGV | Chiller
Compressor 1 Status | Running/Off | CH4COM1S | Chiller
Compressor 1 Motor Speed / VFD Speed | 0-100% | CH4COM1SPD | Chiller
CH4CompDiscSuperheat | °F | CH4CompDiscSuperheat | Chiller
CH4CondApproach | °F | CH4CondApproach | Chiller
CH4DISTEMP | °F | CH4DISTEMP | Chiller
CH4DPLift | PSI | CH4DPLift | Chiller
CH4DTLift | °F | CH4DTLift | Chiller
CH4EvapApproach | °F | CH4EvapApproach | Chiller
Evaporator Refrigerant Pressure | PSI | CH4EVP | Chiller
Evaporator Refrigerant Temperature | °F | CH4EVT | Chiller
Chiller Alarm/Fault Msg | Normal/Alarm | CH4F | Chiller
CH4FLA | 0-100% | CH4FLA | Chiller
Total Chiller kW | kW | CH4kW | Chiller
CH4PctLoad | % | CH4PctLoad | Chiller
CH4Ready | True/False | CH4Ready | Chiller
Chiller Status | Running/Off | CH4S | Chiller
CH4SBoolean | Running/Off | CH4SBoolean | Chiller
Chiller Start/Stop | Enable/Disable | CH4SS | Chiller
CH4SURGE | True/False | CH4SURGE | Chiller
CH4SURGECNT | Value | CH4SURGECNT | Chiller
CH4Tons | Ton | CH4Tons | Chiller
CH4W$2fTon | kW/Ton | CH4W$2fTon | Chiller
Chiller 5 CHWSTSP Alarm | Normal/Alarm | CH5_CHWSTSP_Alarm | Chiller
Chiller Failed (BAS Alarm) | Normal/Alarm | CH5ALARM | Chiller
CH5AVAIL | True/False | CH5AVAIL | Chiller
CH5Calc_ProjkW$2fTon | kW/Ton | CH5Calc_ProjkW$2fTon | Chiller
Condenser Refrigerant Pressure | PSI | CH5CDP | Chiller
Condenser Refrigerant Temperature | °F | CH5CDT | Chiller
CH5CDW_DeltaT | °F | CH5CDW_DeltaT | Chiller
Condenser Return Water Temperature | °F | CH5CDWRT | Chiller
Condenser Supply Water Temperature | °F | CH5CDWST | Chiller
Chiller CDW Valve Command (Binary) | Open/Close | CH5CDWVLV | Chiller
CH5CHW_DeltaT | °F | CH5CHW_DeltaT | Chiller
Chiller Evaporator Flow | GPM | CH5CHWFLO | Chiller
Chilled Water Return Temperature | °F | CH5CHWRT | Chiller
Chilled Water Supply Temperature | °F | CH5CHWST | Chiller
Chilled Water Supply Temperature Setpoint | °F | CH5CHWSTSP | Chiller
Chiller CHW Valve Command (Binary) | Open/Close | CH5CHWVLV | Chiller
Compressor 1 General Fault | Normal/Alarm | CH5COM1F | Chiller
Compressor 1 IGV position / Vane Position | 0-100% | CH5COM1IGV | Chiller
Compressor 1 Status | Running/Off | CH5COM1S | Chiller
Compressor 1 Motor Speed / VFD Speed | 0-100% | CH5COM1SPD | Chiller
CH5CompDiscSuperheat | °F | CH5CompDiscSuperheat | Chiller
CH5CondApproach | °F | CH5CondApproach | Chiller
CH5DISTEMP | °F | CH5DISTEMP | Chiller
CH5DPLift | PSI | CH5DPLift | Chiller
CH5DTLift | °F | CH5DTLift | Chiller
CH5EvapApproach | °F | CH5EvapApproach | Chiller
Evaporator Refrigerant Pressure | PSI | CH5EVP | Chiller
Evaporator Refrigerant Temperature | °F | CH5EVT | Chiller
Chiller Alarm/Fault Msg | Normal/Alarm | CH5F | Chiller
CH5FLA | 0-100% | CH5FLA | Chiller
Total Chiller kW | kW | CH5kW | Chiller
CH5kW$2fTon | kW/Ton | CH5kW$2fTon | Chiller
CH5PctLoad | % | CH5PctLoad | Chiller
CH5Ready | True/False | CH5Ready | Chiller
Chiller Status | Running/Off | CH5S | Chiller
CH5SBoolean | On/Off | CH5SBoolean | Chiller
Chiller Start/Stop | Enable/Disable | CH5SS | Chiller
CH5SURGE | True/False | CH5SURGE | Chiller
CH5SURGECNT | Value | CH5SURGECNT | Chiller
CH5Tons | Ton | CH5Tons | Chiller
CDWP Failed (BAS Alarm) | Normal/Alarm | CDWP3Failed | Condenser Water Pump
CDWP3HZ | Hz | CDWP3HZ | Condenser Water Pump
CDWP kW | kW | CDWP3kW | Condenser Water Pump
CDWP Status | Running/Off | CDWP3S | Condenser Water Pump
CDWP Speed Setting | 0-100% | CDWP3SPD | Condenser Water Pump
CDWP3SPD Alarm | Normal/Alarm | CDWP3SPD_Alarm | Condenser Water Pump
CDWP Start/Stop | Enable/Disable | CDWP3SS | Condenser Water Pump
CDWP Failed (BAS Alarm) | Normal/Alarm | CDWP4Failed | Condenser Water Pump
CDWP4HZ | Hz | CDWP4HZ | Condenser Water Pump
CDWP kW | kW | CDWP4kW | Condenser Water Pump
CDWP Status | Running/Off | CDWP4S | Condenser Water Pump
CDWP Speed Setting | 0-100% | CDWP4SPD | Condenser Water Pump
CDWP4SPD Alarm | Normal/Alarm | CDWP4SPD_Alarm | Condenser Water Pump
CDWP Start/Stop | Enable/Disable | CDWP4SS | Condenser Water Pump
CDWP Failed (BAS Alarm) | Normal/Alarm | CDWP5Failed | Condenser Water Pump
CDWP5HZ | Hz | CDWP5HZ | Condenser Water Pump
CDWP kW | kW | CDWP5kW | Condenser Water Pump
CDWP Status | Running/Off | CDWP5S | Condenser Water Pump
CDWP Speed Setting | 0-100% | CDWP5SPD | Condenser Water Pump
CDWP5SPD Alarm | Normal/Alarm | CDWP5SPD_Alarm | Condenser Water Pump
CDWP Start/Stop | Enable/Disable | CDWP5SS | Condenser Water Pump
Cooling Tower 4 Entering Water Isolation Valve (Binary) | Open/Close | CT4EVLV | Cooling Tower Cell
Cooling Tower Fan Failed (BAS Alarm) | Normal/Alarm | CT4Failed | Cooling Tower Cell
CT4HZ | Hz | CT4HZ | Cooling Tower Cell
CT Fan kW | kW | CT4kW | Cooling Tower Cell
CT Fan Status | Running/Off | CT4S | Cooling Tower Cell
CT Fan Speed Setting | 0-100% | CT4SPD | Cooling Tower Cell
Cooling Tower 4 SPD Alarm | Normal/Alarm | CT4SPD_Alarm | Cooling Tower Cell
CT Fan Start/Stop Command | Enable/Disable | CT4SS | Cooling Tower Cell
Cooling Tower 5 Entering Water Isolation Valve (Binary) | Open/Close | CT5EVLV | Cooling Tower Cell
Cooling Tower Fan Failed (BAS Alarm) | Normal/Alarm | CT5Failed | Cooling Tower Cell
CT5HZ | Hz | CT5HZ | Cooling Tower Cell
CT Fan kW | kW | CT5kW | Cooling Tower Cell
CT Fan Status | Running/Off | CT5S | Cooling Tower Cell
CT Fan Speed Setting | 0-100% | CT5SPD | Cooling Tower Cell
Cooling Tower 5 SPD Alarm | Normal/Alarm | CT5SPD_Alarm | Cooling Tower Cell
CT Fan Start/Stop Command | Enable/Disable | CT5SS | Cooling Tower Cell
Optimal Control | On/Off | OptimumControl | Summary